## Slide 2: Nuclear Power Plant Gösgen-Däniken LTD
Built in 1979, Switzerland
1035 MW PWR
3 Loops, KWU Design
Emergency Systems: HPIS (4 pumps), 6 Accumulators, LPIS (4 pumps), EFWS (4 pumps), 4 Diesel Generators
Special Emergency Systems: SEFW (2 pumps), SECC (2 pumps), 2 Diesel Generators
Containment: Double (Steel & Concrete), UPES, CFVS
Notes: KKG has almost 40 years, but it is featured and upgraded by the most advanced, independent and redundant safety systems.

## Slide 3: Full-Scope PSA Level 3 Of NPP Gösgen
Nuclear Power Plant (KKG) PSA Model Features
KKG PSA Level 1 and Level 2
PSA Level 3 – Model
KKG PSA Level 3 – Selection of Accident Scenarios
Interface Level 1 and Level 2 PSA to Level 3 PSA
Nuclear Power Plant PSA Model Features

## Slide 4: KKG PSA Level 3 - Latest Developments and Results “USNRC - IMUG 2020”
Kernkraftwerk Gösgen Däniken AG
Däniken
September 02, 2020

## Slide 5: KKG PSA Level 3 - Latest Developments and Results
New Meteorological Databases
Meteorological Data Impact on
  Dispersion and Contamination
  Health Effects
Fully Coupled PSA Level 3 Results
PSA 2D Plots Generator (based on Phyton)
Emergency Planning Applications
On-Site Dose Assessment using CFD-based models
Contents

## Slide 6: KKG PSA Level 3 - Latest Developments and Results
New Meteorological Databases
  Historical data 20 years hourly records, 1989 - 2008
  2011 hourly records
  2018 hourly records
  New boundary layer height, based on the ETHZ measured data
New Meteorological Databases

## Slide 7: KKG 2018 Windrose

## Slide 8: KKG PSA Level 3 - Latest Developments and Results
Boundary layer height using the ETHZ Pathfinder-TURB algorithm
  The algorithm analyzes the ceilometer backscatter data and the real-time detection of the vertical structure of the planetary boundary layer
  Providing an accurate evaluation of the boundary layer height.
New Meteorological Databases:
ETHZ Pathfinder-TURB Algorithm

## Slide 9: KKG PSA Level 3 - Latest Developments and Results
Meteorological Data Impact: Dispersion and Contamination
Results based on two sets of meteorological data (year 2011 and 2018) were compared. It has been found that:
  The meteorological data can cause difference in the results up to 38%.
  Boundary layer model (ETHZ Pathfinder-TURB algorithm) can also cause a difference in results of 32%.
Meteorological Data Impact

## Slide 10: KKG PSA Level 3 - Latest Developments and Results
Meteorological Data Impact: Health Effects
Early fatalities in 2011 were substantially higher than 2018 (up to one order of magnitude). The early fatalities were confirmed to be very small and very closed to the plant.
Although the cancer fatalities between 0 – 2 km were higher in 2011, the difference in the fatalities remained very small.
Meteorological Data Impact

## Slide 11: KKG PSA Level 3 - Latest Developments and Results
Meteorological Data Impact: Health Effects
Two boundary layer models (original model and Pathfinder-TURB) were tested for the year 2018 meteorological data.
The early fatalities were not affected by the boundary layer height model.
The difference between the cancer fatalities evaluated by implementing the two boundary layer models were small (less than 14.5%)
Meteorological Data Impact

## Slide 12: KKG PSA Level 3 - Latest Developments and Results
Fully Coupled PSA Leve 3 Results
A model have been developed for coupling PSA level 3 results to PSA Level 1&2
It links the PSA Level 3 conditional probabilities to PSA Level 1&2 release frequencies
The results are presented in terms of Frequency of Exceedance (FoE)
Examples are provide for the MAC and TSBO severe accidents
Fully Coupled PSA Leve 3 Results

## Slide 13: KKG PSA Level 3 - Latest Developments and Results
Fully Coupled PSA Leve 3 Results

## Slide 14: KKG PSA Level 3 - Latest Developments and Results
Fully Coupled PSA Leve 3 Results

## Slide 15: KKG PSA Level 3 - Latest Developments and Results
Fully Coupled PSA Leve 3 Results

## Slide 16: KKG PSA Level 3 - Latest Developments and Results
PSA 2D Plots Generator
It is written in Phyton. No need for any external support libraries or installations.
Several plots can be obtained automatically for a given case, such as:
  Dose
  Intervention Level
  Air and ground Contamination (from Cs-137, I-131, Pu-241, Sr-89, and U-237)
PSA 2D Plots Generator (based on Phyton)

## Slide 17: KKG PSA Level 3 - Latest Developments and Results
PSA 2D Plots Generator
MAC 2019 Results: Dose, 5km

## Slide 18: KKG PSA Level 3 - Latest Developments and Results
PSA 2D Plots Generator
MAC 2019 Results: Intervention Level

## Slide 19: KKG PSA Level 3 - Latest Developments and Results
PSA 2D Plots Generator
MAC 2019 Results: Dose, 50 km

## Slide 20: KKG PSA Level 3 - Latest Developments and Results
PSA 2D Plots Generator
MAC 2019 Results: Air Contamination Cs-137

## Slide 21: KKG PSA Level 3 - Latest Developments and Results
PSA 2D Plots Generator
MAC 2019 Results: Total ground Contamination

## Slide 22: KKG PSA Level 3 - Latest Developments and Results
Emergency Planning Applications
Estimation of the dose and contamination level in a broad area
Detailed information's within the Swiss two emergency zones (<5km & <20 km), and beyond (>20 km)
First estimation of the Swiss Intervention Levels, covering:
  Staying in house
  Staying in cellars
  Use of Swiss Shelters
  Evacuation
Countermeasures
  Short-term actions
  Long-term actions
Emergency Planning Applications

## Slide 23: KKG PSA Level 3 - Latest Developments and Results
CFD-based On-Site Dose Assessment
Why CFD based?
  Because WinMACCS, RASCAL or other Gaussian family based model do not provide the necessary and detailed information for the On-Site Emergency Planning.
  Moreover, a realistic model of the plant buildings and the site is fundamental for the on site actions within and beyond the plant mission time (72 hours).
  To provide an accurate estimation of the ground concentration of the released radioisotopes and the dose rates at more significant locations of interest for the On-Site Emergency Planning (ground level, roof of the buildings, and below the cooling tower).
On-Site Dose Assessment using CFD-based models

## Slide 24: KKG PSA Level 3 - Latest Developments and Results
KKG On-Site Dose Assessment Model
It has:
A realistic model of the plant buildings
A Site model including details (from GIS) of hills, valleys, forest, … Identified neighboring towns, roads, rail-roads, escape ways.
It is featured by:
CFD evaluations of the wind flow
Particle tracking simulations and determination of radioisotope group ground concentration
3D dose assessment
3D representation wind flow, dose rates
Ground level concentrations and doses
On-Site Dose Assessment using CFD-based models

## Slide 25: KKG PSA Level 3 - Latest Developments and Results
On-Site Dose Assessment using CFD-based models

## Slide 26: KKG PSA Level 3 - Latest Developments and Results
On-Site Dose Assessment using CFD-based models
KKG Site

## Slide 27: KKG PSA Level 3 - Latest Developments and Results
On-Site Dose Assessment using CFD-based models
Wind speed contours at Z=+5 m

## Slide 28: KKG PSA Level 3 - Latest Developments and Results
On-Site Dose Assessment using CFD-based models
Wind streamlines at Z=+5 m

## Slide 29: KKG PSA Level 3 - Latest Developments and Results
On-Site Dose Assessment using CFD-based models
Wind velocity Vectors at Z=+5 m

## Slide 30: KKG PSA Level 3 - Latest Developments and Results
On-Site Dose Assessment using CFD-based models
Other results coming soon!!!

## Slide 31: Thank you for your attention
NPP Gösgen LTD & SST SwissSafeTech AG LTD